YE3 SERIES CAST IRON THREE PHASE ELECTRIC MOTORS

GENERAL INTRODUCTION

YE3 series electric motors (center height H 80-400 mm, 0.75kw - 315kw) are designed for Directive 2005/32/EC of the European Parliament and of the Council of 6 July 2005 And meets energy- using products and amending Council Directive 92/42/EEC and Directives 96/57/EC and 2000/55/EC of the European Parliament and of the Council, Commission regulation (EC) No 640/2009 of 22 July 2009.

Standard Features:

1.  Three Phase, Europe/Australia Voltage:  220/380V, 230/400V, 240/415V   Up to 3KW;

380/660V, 400/690V, 415V/720   4Kw and Above;

50/60HZ,   IP55,  Class F, TEFC ;

2.   Cast Iron Frames 80-400,

3.   Squirrel Cage Rotor/Aluminum Die Cast

4.   V-Ring On Both End-Shields Or Oil-Seal Ring On Both End-Shields

5.   Anti-Condensation Drain Holes On Request

6.   IE3 Design: 2P, 4P, 6P, 8P, 10P

7.   Class "F" Insulation

8.   Continuous Duty-S1

9.   Ambient Temp. 40℃

10.  Altitude: 1000M

11.  Dimensions According To IEC-72

12.  Performance According To IEC-34

13.  Regreasing Nipples From 180 And Above

14.  Metric Thread Cable Entries In Terminal Box

15.  PTC Thermistors(1 Per Phase) fitted in 160M and Above

16.  Suitable For Inverter Duty Applications

17.  Paint Color Blue: RAL5010 Or Others

Optional Features:

1.  Degree of Protection : IP56

2.  Bearing Seals: Oil Seal Or Labyrinth Seal For 160 And Above

3.  Thermal Protection:   1.RTD-PT100

2. PTC For Frame 132 And Below

4.  Space Heaters

5.  Class "H" Insulation

6.  Roller Bearing For Frame 160M and Above.

7.  Hollow Shaft , Stainless Steel Shaft And Special Shaft.

YE3  MOTORS POWER TO SPEED IS AS SHOWN IN TABLE 1: TALBE 1：

| Frame | Synchronous speed rpm |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 3000 | 1500 | 1000 | 750 | 600 |
|  | Rated output kW |  |  |  |  |
| 801 | 0.75 | 0.55 | 0.37 | 0.18 | - |
| 802 | 1.1 | 0.75 | 0.55 | 0.25 | - |
| 90S | 1.5 | 1.1 | 0.75 | 0.37 | - |
| 90L | 2.2 | 1.5 | 1.1 | 0.55 | - |
| 100L1 | 3 | 2.2 | 1.5 | 0.75 | - |
| 100L2 |  | 3 |  | 1.1 | - |
| 112M | 4 | 4 | 2.2 | 1.5 | - |
| 132S1 | 5.5 5 | 5.5 | 3 | 2.2 | - |
| 132S2 | 7.5 |  |  |  | - |
| 132M1 | - | 7.5 | 4 | 3 | - |
| 132M2 |  |  | 5.5 |  | - |
| 160M1 | 11 | 11 | 7.5 | 4 | - |
| 160M2 | 15 |  |  | 5.5 | - |
| 160L | 18.5 | 15 | 11 | 7.5 | - |
| 180M | 22 | 18.5 | - | - | - |
| 180L | - | 22 | 15 | 11 | - |
| 200L1 | 30 | 30 | 18.5 | 15 | - |
| 200L2 | 37 |  | 22 |  | - |
| 225S | - | 37 | - | 18.5 | - |
| 225M | 45 | 45 | 30 | 22 | - |
| 250M | 55 | 55 | 37 | 30 | - |
| 280S | 75 | 75 | 45 | 37 | - |
| 280M | 90 | 90 | 55 | 45 | - |
| 315S | 110 | 110 | 75 | 55 | 45 |
| 315M | 132 | 132 | 90 | 75 | 55 |
| 315L1 | 160 | 160 | 110 | 90 | 75 |
| 315L2 | 200 | 200 | 132 | 110 | 90 |
| 355M1 | 250 | 250 | 160 | 132 | 110 |
| 355M2 |  |  | 200 | 160 | 132 |
| 355L | 315 | 315 | 250 | 200 | 160 |
| 400M,L | 355 | 355 | 315 | 250 | 180 |
|  | 400 | 400 | 355 | 280 | 200 |
|  | 450 | 450 | 400 | 315 | 250 |
|  | 500 | 500 | 450 | 355 | 280 |
|  | 560 | 560 | 500 | 400 | 315 |

MOUNTING ARRANGEMENTS

There are five basic constructional mounting arrangements for series C motors:

B3: Frame with feet, end bracket without flange.

B5: Frame without foot, end bracket with flange (with hole)

B35: Frame with feet, end bracket with flange (with hole)

B34: Frame with feet, end bracket with flange (with screw)

B14: Frame without foot, end bracket with flange (with screw)

The commonly used mounting arrangements and the corresponding frame no.are shown as follows in TABLE 2：

BEARING

TABLE 3：     The Bearing No. For Motors Are As Shown In Table 3:

| Frame No. | Driving end |  | Non-driving end |  |
| --- | --- | --- | --- | --- |
|  | 2P | 4P.6P.8P.10P | 2P | 4P.6P.8P.10P |
| 80 | 6204-2RZ |  | 6204-2RZ |  |
| 90 | 6205-2RZ |  | 6205-2RZ |  |
| 100 | 6206-2RZ |  | 6206-2RZ |  |
| 112 | 6306-2RZ |  | 6306-2RZ |  |
| 132 | 6308-2RZ |  | 6308-2RZ |  |
| 160 | 6309-2RZ |  | 6309-2RZ |  |
| 180 | 6311 | 6311 | 6311 |  |
| 200 | 6312 | 6312 | 6312 |  |
| 225 | 6312 | 6313 | 6312 |  |
| 250 | 6313 | 6314 | 6313 |  |
| 280 | 6314 | 6317 | 6314 |  |
| 315 | 6317 | N319 or 6319 | 6317 | 6319 |
| 355 | 6319 or 6317 | N322 or 6322 | 6319 or 6317 | 6322 |
| 400 | 6317 | N326 or 6326 | 6317 | 6326 |

NOISE

Please Specify The Required Noise Levels According To Table 4 Below When Order.     TABLE 4：

| Output (kW) | Synchronous Speed （RPM） |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3000 |  | 1500 |  | 1000 |  | 750 |  | 600 |  |
|  | Sound Power Level dB(A) |  |  |  |  |  |  |  |  |  |
|  | No Load | Load | No Load | Load | No Load | Load | No Load | Load | No Load | Load |
| 0.75 | 67 | 69 | 58 | 63 | 57 | 64 | 59 | 67 | - | - |
| 1.1 | 67 | 69 | 61 | 66 | 57 | 64 | 59 | 67 | - | - |
| 1.5 | 72 | 74 | 61 | 66 | 61 | 68 | 61 | 69 | - | -- |
| 2.2 | 72 | 74 | 64 | 69 | 65 | 72 | 64 | 72 | - | - |
| 3 | 76 | 78 | 64 | 69 | 69 | 76 | 64 | 72 | - | - |
| 4 | 77 | 79 | 65 | 70 | 69 | 76 | 68 | 76 | - | - |
| 5.5 | 80 | 82 | 71 | 76 | 69 | 76 | 68 | 76 | - | - |
| 7.5 | 80 | 82 | 71 | 76 | 73 | 80 | 68 | 76 | - | - |
| 11 | 86 | 88 | 75 | 80 | 73 | 80 | 70 | 78 | - | - |
| 15 | 86 | 88 | 75 | 79 | 73 | 79 | 73 | 81 | - | - |
| 18.5 | 86 | 88 | 76 | 80 | 76 | 82 | 73 | 80 | - | - |
| 22 | 89 | 91 | 76 | 80 | 76 | 82 | 73 | 80 | - | - |
| 30 | 92 | 94 | 79 | 83 | 76 | 82 | 75 | 82 | - | - |
| 37 | 92 | 94 | 81 | 85 | 78 | 84 | 76 | 83 | - | - |
| 45 | 92 | 94 | 81 | 84 | 80 | 85 | 76 | 82 | 82 | 89 |
| 55 | 93 | 95 | 83 | 86 | 80 | 85 | 82 | 88 | 82 | 89 |
| 75 | 94 | 94 | 86 | 89 | 85 | 90 | 82 | 88 | 82 | 89 |
| 90 | 94 | 94 | 86 | 89 | 85 | 90 | 82 | 88 | 82 | 89 |
| 110 | 96 | 98 | 93 | 96 | 85 | 90 | 82 | 88 | 90 | 97 |
| 132 | 96 | 98 | 93 | 96 | 85 | 89 | 90 | 95 | 90 | 96 |
| 160 | 99 | 101 | 97 | 100 | 92 | 96 | 90 | 95 | 90 | 96 |
| 200 | 99 | 101 | 97 | 100 | 92 | 96 | 90 | 95 | - | - |
| 250 | 103 | 105 | 101 | 104 | 92 | 96 | 90 | 95 | - | - |
| 315 | 103 | 105 | 101 | 104 | 96 | 100 | 90 | 95 | - | - |
| 355 | 105 | 108 | 105 | 108 | 96 | 100 | 95 | 99 |  |  |
| 400 | 105 | 108 | 105 | 108 | 96 | 100 | 95 | 99 |  |  |

VIBRATION

At No-load The R.M.S Values Of The Vibration Velocity (i.e. The Limits Of Vibration Severity) Of Motors Should Not Exceed The Values Of Class N. Specified In Table 5. Class R、S. Is Available On Request.

TABLE 5

| Frame size | ≤132 |  |  | ＞132~225 |  | ＞225~400 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| r/min | 600~1800 | >1800~3600 |  | 600~3600 | >1800~3600 | 600~1800 | >1800~3600 |
| CALSS OF VIBRATION | mm/s the R.M.S value of the vibration velocity |  |  |  |  |  |  |
| N | 1.8 |  | 2.8 |  |  | 3.5 |  |
| R | 0.71 | 1.12 | 1.12 |  | 1.80 | 1.80 | 2.80 |
| S | 0.45 | 0.71 | 0.71 |  | 1.12 | 1.12 | 1.80 |

TERMINAL BOX

The normal position of the terminal box is on the top. But may be arranged on the left-hand side or on the right-hand side if specified when ordering. The power cable can be let out through the outlet of the terminal box in four directions by turning the box at any one of the four positions with 90 interval . There is a sealing construction (Metric Cable Glands）at the outlet (for details, see figure). And there is a M15*1.5 screw and cable glands at one side of terminal box in YE3-160 ~ YE3-400. It is used for letting out the control cable.

The Metric table glands, the Dia. Of the outlet holes and the pipe threads for the frame numbers are as shown in table 6：

TABLE  6：

| FRAME NO. | METRIC CABLE GLANDS | X*Y*Z mm |
| --- | --- | --- |
| YE3-80 | 1-M20*1.5 | 92*92*44 |
| YE3-90～YE3-100 | 2-M20*1.5 | 100*100*49 |
| YE3-112～YE3-132 | 2-M25*1.5 | 112*112*56 |
| YE3-160～YE3-180 | 2-M36*2 | 150*160*105 |
| YE3-200～YE3-225 | 2-M48*2 | 188*208*105 |
| YE3-250～YE3-280 | 2-M64*2 | 216*251*120 |
| YE3-315 | 2-M64*2 | 300*358*198 |
| YE3-355 | 2-M72*2 | 330*380*200 |
| YE3 -400 | 3-M72*2 | 430*545*275 |

DEGREE OF PROTECTION

The series motors adopts IP55 degree of protection, and lubricate facility is applied to center height H180-400.